## LV Automatic Power Factor Correction and  Detuned Filter Bank

### General

SUMARY

This section included Power and Automatic Power Factor Correction and Filter Bank.

Automatic Power Factor Correction shall be ___ kVAR switching steps of ____ kVARS for the _ _  x  _____ kVAR unit.

The complete equipment shall be pre-wired and factory assembled, including main terminal lugs, a micro-processor programmable controller, individual capacitor stages including current limiting fuses, tuning reactors and contactors cabled to each capacitor bank step. Each bank should have _____kVAR  at  ____ Volts.

The assemblies will be UL listed & CSA approved.

### Enclosure type :  [1, 12 indoor or 3R outdoor]

The capacitor unit shall consist of 12 gauge steel enclosure, EEMAC 1A gasketted, to form a rigid free standing, dead front structure. The access door in front shall be hinged and complete with provision for locking. The door(s) shall have mechanical interlocks through the breaker (optional), so that a door cannot be opened with a unit energized.  An interlock defeater mechanism shall allow intentional access. The removable lifting lugs shall be provided to permit the lifting of the assembled capacitor unit.

The interior of each assembly shall have a unit schematic and wiring diagram.

### Capacitors

The capacitors shall be dry type, low loss (0.5W per kVAR), self healing dielectric with special heat transfer package. An Internal end of life fuse shall be included in each capacitor cell. The discharge resistors shall drain residual voltage to 50V or less within one minute of de-energization.

Capacitor design shall be rated for 135% continuous over voltage and 165% continuous overcurrent to accommodate the series filter reactor and the harmonics contents. Operating temperatures will be [minus] 40 degrees celcius to (plus) 40 degrees celcius. Oil design cells containing flammable liquid and pressure sensitive interrupters will not be allowed.

Each unit will be comprised of individual cells mounted in a common free standing steel enclosure internally interconnected to three external terminal bushings. Cells will not be exposed within the bank enclosure. Trays of individual cells will not be allowed.

The individual cell will be supplied with a special direct heat transfer process to directly remove core heat to ensure cooler operation for increased performance.

Individual capacitor assemblies will be supplied with a light beige epoxy powder paint finish.

Use DSHI dry self healing capacitor technology. The Capacitors shall be fitted with correctly sized current limiting fuses at minimum 165 % of nominal current complete with external Blown Fuse Indicator lights".

### Tuning Reactors

Tuning reactors for each capacitive stage shall be selected such that filter tuning of each stage is equal to 4.1 x 60 Hertz (245 Hertz).

Reactor shall be constructed of EI laminated low hysteresis core with a controlled air gap and three copper windings of rectangular cross section glass insulated copper conductor.

Reactor assembly shall be impregnated with high temperature thermo-setting insulation material.  Reactor insulation shall be rated for 115 Deg C rise over a 40 Deg C ambient class H (180.C).

Center leg of tuning reactor shall have an embedded thermistor to deenergize the associated contactor in the event of overheating.

### Control Hardware

- Contactors shall be capacitor switching rated for 10 million operations and rated at  135% of nominal current.

- Current limiting fuse 200 ka 600 Volts class per phase (3).

- Control transformer 480/ 120 volts 500 VA c/w primary and secondary fuses protections.

Control Power Requirements

- 120V control circuit transformer shall be provided within the enclosure.

- All major components including both primary and secondary transformer shall be fused.

- The control circuit shall be protected by a resettable Class A ground fault protection breaker.

- A shorting terminal shall be provided for two incoming current transformer wires.  A single current transformer to be installed upstream of where the automatic capacitor is attached to the electrical distribution system, shall be provided with a ratio of [      ] to 5 Amperes.  The CT shall be split core type with an opening large enough to facilitate installation on the cable or buss3.

Optional devices:

- Provide the Breaker with door handle operating mechanism and door interlock. The breaker interrupting capacity shall be  65 kA 480V. or  35 ka 600V (on rating above 250Amp.)..  Bus bracing and components shall be rated for 65kA fault capacity at 30 kV BIL. Fuses rated at 200KA interrupting capacity shall be installed on each phase of each step.

- Provide Current transformer split core type with ratio ….. / 5A. to suit sensing. Current Transformer (CT) ratios commonly available include the following:  500/5, 800/5, 1000/5, 1200/5, 1600/5, 2000/5, 2500/5, 3000/5, 4000/5 and 5000/5.  CT ratio is determined by the current rating of the upstream switchgear to which the capacitor bank is connected.  For instance, a capacitor bank connected to a 2000Amp rated switchboard would require a 2000/5A current transformer.  CT sizing is NOT a function of the size of the capacitor bank or the feeder breaker to the capacitor bank.  Normal split core CT’s have a 4”x7” window which is typically suitable for switchgear rating up to 4000A.  4”x11” window CT’s are also available for higher rating switchgears.

### Controller  Model # NC12

The Control permit selection of a target power factor, adjustable to any value between 0.90 lagging to leading P.F. Controls continuously sense the P.F. on circuits being and, when the power factor differs from the target setting with programmable switched time operation (close and open contactor).

120V control circuit transformation shall be provided within the enclosure.

A shorting terminal shall be provided for two incoming current transformer wires. The Multi-step programmable solid state power factor control equipment shall be designed to automatically maintain desired power factor level, adjusting to system load requirements in selected kVAR steps.  The solid state control shall respond to a current signal from the current transformer on costumer bus and the voltage signal from a potential transformer included in the equipment with a built-in adjustable time delay.

An ON power indication and AUTOMATIC / MANUAL override control shall be provided.

A Liquid Crystal Display of power factor and alarms (12) types shall be provided. Indication of stage energization and inductive / capacitive condition shall be provided. The control will display the measurement of : P.F., Voltage, Current, kW, kVA, kVAR, THD I, THD E, Alarms (12), No steps, override status, frequency, …etc

An alarm dry contact closure shall be provided in the event that target power factor is not met, power to the controller has been lost or CT current is too high/low, temperature exceeds preset limits or a system over voltage condition occurs. The Alarm group will be :

- Low P.F.

- Hunting

- Abnormal P.F.

- Low Voltage

- Over P.F. compensation

- Wrong Frequency

- Over Current

- Over Voltage

- Over Temperature

- THD V

- Capacitor overload

- Capacitor output low

An automatic shutdown and systematic re-staging of capacitor stages shall be provided in the event of a power loss, high internal system temperatures, a system under voltage, over voltage, resonance or high harmonic content condition.

# TECHNICAL INFORMATION REQUIRED

## Required with proposal:

- Dimensioned outline drawings showing overall and individual component forming part of the substation or equipment.

- Schedule of deliveries of equipment including date of first arrival, arrival sequence and date of last arrival.

- List of major components including sizes and weights

- Cable termination details

- Completed Data sheets (Attached)

Shop Drawings:

Detail equipment assemblies and indicate dimensions, weights, method of factory assembly, components and locations and size of each field connection. Show the cable access and workspace and clearance.

# PERFORMANCE REQUIREMENTS

## Warranty

The supplier shall guarantee the equipment for a period of 18 months from the delivery or 12 months from the commissioning, whichever occurs first.

## Start-Up Assistance

The tender shall include start-up assistance as required normally for equipment of this type. This means that a capable factory representative with intimate knowledge of the equipment supplied shall be available for assistance on the site immediately prior to and during start-up. State the amount of time included. The tender shall also include the cost per day for time longer than this, if the request is made during the start-up.

# Quality control, TESTS AND INSPECTIONS

The supplier shall be ISO 9001 – 2000 production certified.

The supplier shall provide with this bid the test procedures that he proposes to be used to document and establish “Final Acceptance”.

Prior to shipment all units shall be properly assembled and tested completely in order to ensure operation in accordance with UL and CSA requirements. Test certificates to be supplied with final drawings. A final witness test may be made by the Purchaser or his representative prior to shipment.

10. Construction Standards

The Capacitors Bank has been designed to the following standards:

UL ..............................  Underwriters Laboratories

CSA ............................ Canadian Standards Association

IEEE 519-1992 ........... Guide for Harmonic Content.

NEMA ......................... National Electrical Manufacturers

Association ANSI .........American National Standards Institute

ISO 9001-2008 ……… Quality Control Certification

- Installation :

All equipment will be installed and tested as NEC and CEC code requirements. Acceptable Manufacturer and Product will be Gentec FT100 series ..